TYPICAL SPECIFICATION

6800 Intelligent Variable Speed Design Envelope

- PART 1- GENERAL

Quality Assurance

Single-Source Responsibility for complete package. The entire package shall be third party certified by Underwriters Laboratories Inc.

Design Criteria

The drawings indicate sizes, profiles, connections and dimensional requirements of plumbing pumps and are based on the specific manufacturer types and models indicated. Pumps having equal performance characteristics by other manufacturers may be considered, provided that deviations in dimensions and profiles do not change the design intent and performance as judged by the engineer. The burden of proof for equality is on the proposer.

Delivery and Storage

Store pumps in a dry location. Retain shipping flange protective covers and protective coatings during storage. Protect bearings and couplings against damage from sand, grit and other foreign matter. Comply with manufacturers' rigging instructions for handling.

- PART II: PRODUCTS

Domestic Water Booster System

Provide an Armstrong Series 6800 IVS Design Envelope Packaged Booster System model _______.  The design envelope shall encompass an initial design point of ______ USgpm (Lps) at _____ psi (kPa) head.  The design envelope shall also be capable of supplying ______USgpm (Lps) at _____ psi (kPa) head at ____% minimum efficiency level.

Pumps

Each Vertical MultiStage (VMS) pump, with pump characteristics which provide rising heads to shut off, shall be supplied with a ____hp, ODP (TEFC), ____v/3/60, NEMA Premium® efficiency motor and an Armstrong UL Type-12 enclosure variable speed drive, which shall be integrated with the motor.  Drives shall not be enclosed within the control panel.

Variable speed drives supplied shall have the following features: VVC-PWM type providing near unity displacement power factor (cos ) without the need for external power factor correction capacitors at all loads and speeds, DC link chokes for the reduction of mains borne harmonic currents to reduce the DC link ripple current thereby increasing the DC link capacitors lifetime, UL and C-UL Listed & CE Marked showing compliance with both the EMC Directive 89/336/EEC and the Low Voltage Directive 72/23/EEC, RFI filters incorporated within the drive to ensure it meets the emission and immunity requirements of EN61800-3 to the 1st Environment Class C1 (EN55011 unrestricted sales class B), VFD and motor protection shall include: motor phase to phase fault, motor phase to earth fault, loss of supply phase, over voltage, under voltage, motor over temperature, inverter overload, over current.

Materials of Construction

Pump

Pump Casing – 304 Stainless Steel with ANSI-250 flanges for working pressure to 370 psig (25 bar) at 250°F (120°C), Cast Iron with ANSI-150 flanges for working pressures to 232 psig (16 bar) at 250°F (120°C) and Cast

Iron with ANSI-300 flanges for working pressures to 400 psig (27 bar) at 250°F (120°C).

Impeller – Stainless Steel, fully enclosed type.

Shaft - Provide Stainless Steel pump shaft.

Coupling - Rigid spacer type of Brass or Steel. Coupling to be designed to allow removal of all mechanical seal components for servicing without removal of the pump.

Mechanical Seals - Mechanical shaft seal with FPM® secondary seal, carbon rotating face and silicon carbide stationary seat.

Packaging

Headers – Stainless Steel.

Base – Stainless Steel.

Panel Support – Stainless Steel

Pump Sequencing

The pump designated as the lead pump shall start after a 5 second On-Delay time after sensing a drop in the desired set point value.  The pump controller shall compare a signal from the discharge pressure transducer to the set point value and the lead pump speed shall ramp up in order to satisfy the set point pressure.  The first lag pump shall start following a 5 second On-Delay time, when the lead pump exceeds its best operating point (BOP), and a minimum run timer shall ensure that the lag pump runs for a minimum of 5 minutes.  The lag pump shall ramp down in speed and turn off when the 2 pumps are running, are operating at a point below the BOP and the lag pump minimum run timer has timed out.  The lead pump shall continue to operate and meet system requirements based on the set point pressure.  These steps shall be repeated in order to satisfy the building requirements for 2, 3, 4 and 5 pump packages. The lead pump shall alternate every 24 hrs of operation where the second pump shall be brought on for a period of 5 seconds, both pumps shall operate and the first pump on shall ramp down.

Lead Pump Shutdown Controls

All systems are equipped with a "No-Flow" shutdown that will stop the pumps when the pump controller determines there has been a "No-Flow" condition for a continuous 5-minute period.  The lead pump will start again once a drop in pressure of at least 5 PSI is measured on the discharge of the system. The system can be manually operated by means of the virtual HOA selector buttons provided on the operator interface.

Control Panel

The control panel shall be of the programmable logic controller (PLC) type.  The complete control panel assembly and all internal devices shall be UL508 and/or CSA labeled.  The panel shall be complete with NEMA 1 enclosure and include door interlocked main disconnect, water tight LCD interface, breaker VFD connections, adjustable time delays, Hand-Off-Auto selector for each pump and min run timers.  The control circuit shall include fault relay circuit to turn on the next pump should the lead pump fail.

The controller must be capable of controlling up to 5 pumps, using a 4-20 mA analogue signal using pressure as the control variable.

Controller design shall include provisions for low flow energy savings, soft fill mode, pressure setback, best-operating-point (BOP) sequencing, end of pump curve protection, 24hr operation automatic alternation of pumps, built-in pump on-delay and minimum run timers, re-settable pump elapsed run time meters, smooth pump starting and sequencing, on-screen field modifiable control and alarm parameters, high suction pressure shutdown and no-flow shutdown with drawdown tank/system optimization.

On-screen alarm display with alarm identification shall be incorporated with the following alarms included:  low and high system pressure alarms, low suction pressure shutdown, pump failure, drive fault, and suction and discharge pressure transmitter failures. The controller shall include on-screen fault description and possible cause information with alarm horn for low and high system pressure alarms.  BMS communication via hard wired signals, three analog outputs 0-10 volts DC for discharge, suction and system boost and five digital contacts for booster on, system alarm, pump running and discharge and suction pressure sensor failure.

Non-volatile factory set parameters must be capable of being restored at any time in the field without requiring any programming device or connection to an external source. The controller must hold software in FLASH memory storage which prevents accidental loss of data due to voltage surge or spike.

All controls to be factory pre-wired and tested in accordance with provisions of the national electrical code. All control wires shall be individually numbered and each component shall be labeled accordingly. All internal wiring shall be Copper stranded, A.W.G. with a minimum 90°F rating. The controller shall bear the UL508 label for industrial controls.

Instrumentation and Controls

Pump system shall be supplied with manifold mounted liquid filled pressure gauges for indicating suction and discharge pressure.

Factory Prefabrication

The system shall be factory prefabricated, including ball or butterfly isolation valves on the suction and discharge of each pump, spring loaded or silent check valves on the discharge as well as 2”, 2.5”, 3", 4", 6", 8” or 10” Stainless Steel headers with threaded, grooved or optional flanged adapter system connections and Stainless Steel base and panel support.  All interconnecting piping shall be stainless steel.  The only field connections required shall be piping to the system headers and one incoming power connection at the control panel.

Factory Test and Certification

The booster system and its component parts shall undergo a complete operational flow test from zero to 100% design flow rate under the specified suction pressure conditions. The system certification shall include copies of the test data as certified by a factory engineer. Performance test certifications should be placed inside the control panel and extra copies with an installation manual. In addition, the entire system shall be third party certified by Underwriters Laboratories Inc. In accordance with OSHA 29 CFR with references to nationally recognized testing laboratories.

Manufacturers

The above specification describes equipment manufactured by Armstrong Pumps Inc., North Tonawanda, NY, USA. Alternate manufacturers of equipment will be considered provided that they are completely equal as to type, capacity and efficiency of pumps and controls. Alternate manufacturers' submittals must be certified by an officer of the company who is proposing that their system complies with the specifications in every detail.